Upgrading the NAS Gateway 500 Single Port HBA to Firmware Level 1.92A1

Prerequisite: Before installing firmware level 1.92A1, you must first install the NAS Gateway 500 AIX 5.2 Technology Level 5200-10 Upgrade.  You can verify whether the TL 5200-10 upgrade is already installed by entering “oslevel –s” at the NAS 500 command line.  If the upgrade in installed, the output will be

“5200-10-04-0750”.  If you install firmware level 1.92A1 before the TL 5200-10 upgrade is installed, AIX will no longer see all its hdisks.

- Enter lsslot –c pci to learn the “fcsn” numbers of the FC HBA ports that need to be updated:

- Enter lsmcode –d fcsn for each port to display each port’s firmware level.  If the level displayed is less than 192101, this firmware upgrade is needed.

- FTP the df1080f9.192101 file in binary mode to the /etc/microcode directory of the NAS 500.  On the NAS 500, run a checksum to verify the integrity of the file:

(/etc/microcode)-->sum df1080f9.192101

54720   685 df1080f9.192101

- Install the firmware, using the following command:

diag –d fcsn –T download

You will see the following panel.  Press Enter.

Next, you will see the following panel.  Press Enter.

Next, you will see the following panel.  Press Enter.

Next, you will see the following panel.  Make sure “M    192101” is highlighted, and press Enter.

You will see this panel:

Next, you should see this panel.  Press Enter.

To run diagnostics on the adapter, enter diag.  You will see the following panel; press Enter.

You will see the following panel;  press Enter.

You will see the following panel;  press Enter.

Use the “down” arrow to scroll down to the adapter you just updated.  Press Enter, then ESC+7 to begin the diagnostic routine.

When the diagnostic routine is finished, you should see the following.  Press Enter, then ESC+0 to exit the diagnostics panel.