Procedure for Installing the Single-Port HBA (Feature Code 6239) 191304 Firmware Upgrade

Please use the following procedure to install the Emulex Single-Port HBA (Feature Code 6239) 191304 (HS1.91X4) firmware upgrade.

1. At the NAS 500 root prompt, enter lsslot –c pci to determine the “fcs” numbers AIX assigned to the adapters’ ports.  Enter lsmcode –d fcsn (n being the “fcs” number) to display each port’s firmware level.  If the level displayed is less than 191304, this firmware upgrade is needed.

2. If you have not already unmounted and varied off all of the NAS 500’s NAS volumes, do so now by entering the following:

/opt/nas/bin/lsvol     # displays mounted NAS volumes

umount  /Vols/volumename     # enter this command for each mounted NAS volume

lspv         # displays the volume group names (nvgnnnnnnnnnnnn) and whether they are          “active”.  For all the volume groups that are “active”, enter:

varyoffvg  nvgnnnnnnnnnnnn

3. ftp the df1080f9.191304 file in binary mode to the /etc/microcode directory of the NAS.  On the NAS, run a checksum to verify the integrity of the file:

(/etc/microcode)--> sum df1080f9.191304

26894   458  df1080f9.191304

4. Enter diag –d fcsn –T download to begin the install process.

This is the first screen you will see.  Press <enter>

You will see this screen next.  Make sure /etc/microcode is highlighted, and press <enter>

You will see the popup box depicted below.  Press <enter>.

Make sure “M   191304” is highlighted, and press <enter>.

During the installation, you will see this panel:

Next, you should see the “successful completion” panel.  It is recommended that you run the diag routine to verify the port is functioning properly.

5. Repeat step 4 for each of the remaining adapter ports.